SURGE PROTECTIVE DEVICE FOR LOW VOLTAGE POWER, CONTROL, DATA, AND SIGNAL SYSTEMS

Effective Date: 06/17/2015

Document Identifier: CM-620-2.7.3-01

Printed copies are for reference only; they are not controlled. Latest version is on-line.

FDOT Traffic Engineering Research Laboratory (TERL) Surge Protective Device (SPD) for Low Voltage Power, Control, Data, and Signal Systems Compliance Matrix	By signing this form, the applicant declares that he/she has read and understands the provisions of Section 620 of the FDOT Standard Specifications for Road and Bridge Construction and all implemented modifications. The requirements listed on this matrix are derived from Section 620, and are the basis for determining a product’s compliance and its acceptability for use on Florida’s roads.

Date:	Click here to enter a date.	Applicant’s Name (print):
Manufacturer:
Item, Model No.:	Signature:

ID No	Section	Requirement	Item Comply? (Yes/No)	Comments (Applicant must provide information as indicated)	TERL Evaluation Method
1	620-2.7.3	Device complies with the functional requirements for all available modes (i.e. power L-N, N-G, L-G; data and signal center pin-to-shield, L-L, L-G, and shield-G where appropriate) as shown below.	Provide product literature, specifications, user manual,or similar information that indicates compliance. (Indicate specific configurations by model number or series).	Document Review
Indicate location of requested information in submittal.
For ID 1.a through 1.g, select "Yes" or "No" in 'Section' column if device is provided for APL inclusion. Select "Yes" or "No" in 'Item Comply?' column to indicate if device meets criteria.
1.a	12 VDC SPD has a clamping voltage of 15-20 V with surge capacity of 5kA per mode (8x20 µs) and a maximum let-through of <150 Vpk.	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT Product Certification Handbook (PCH), section 7.2.	Document Review
Indicate location of requested information in submittal.
1.b	24 VAC SPD has a clamping voltage of 30-55 V with surge capacity of 5kA per mode (8x20 µs) and a maximum let-through of <175 Vpk.	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.
1.c	48 VDC SPD has a clamping voltage of 60-85 V with surge capacity of 5kA per mode (8x20 µs) and maximum let-through of <200 Vpk.	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.
1.d	Coaxial Composite Video SPD has a clamping voltage of 4-8 V with surge capacity of 10kA per mode (8x20 µs) and maximum let-through of <65 Vpk (8x20µs/1.2x50µs; 6kV, 3kA).	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.
1.e	RS422/RS485 SPD supports data rates up to 10 Mbps and has a clamping voltage of 8-15 V with surge capacity of 10kA per mode (8x20 µs) and maximum let-through of <30 Vpk.	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.
1.f	T1 SPD supports data rates up to 10 Mbps and has a clamping voltage of 13-30 V with surge capacity of 10kA per mode (8x20 µs) and maximum let-through of <30 Vpk.	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.
1.g	Ethernet Data SPD supports data rates up to 1 Gbps and has a clamping voltage of 7-12 V with surge capacity of 1kA per mode (10x1000 µs) and maximum let-through of <30 Vpk.	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.
1.h	POE SPD supports data rates up to 1 Gbps and has a clamping voltage of 60-70 V with surge capacity of 5kA per mode (8x20 µs) and maximum let-through of <200 Vpk (100kHz 0.5μs; 6kV, 500A).	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.
2	SPD is UL 497B or UL 497C listed, as applicable, and is listed by an NRTL.	Provide product literature, specifications, user manual, or similar information that indicates compliance. (Indicate specific configurations by model number or series).	Document Review
Indicate location of requested information in submittal.
3	620-2.7.4	SPD is permanently marked with manufacturer name or trademark, part number, and date of manufacture or serial number.	Applicant may provide comments in this field.	Physical Inspection
4	All parts are made of corrosion-resistant materials, such as plastic, stainless steel, anodized aluminum, brass, or gold-plated metal.	Provide product literature, specifications, user manual, or similar information that indicates compliance. (Indicate specific configurations by model number or series).	Document Review and Physical Inspection
Indicate location of requested information in submittal.
5	620-2.7.5	SPD operates properly during and after being subjected to the temperature and humidity test described in NEMA TS 2, Section 2.2.7, and the vibration and shock tests described in NEMA TS 2, Sections 2.2.8., and 2.2.9.	Provide a first or third-party test report that demonstrates the device meets this requirement. The test report must meet the requirements of FDOT PCH, section 7.2.	Document Review
Indicate location of requested information in submittal.