|  | FDOT Traffic Engineering Research Laboratory (TERL) Surge Protective Device (SPD) for 120V or 120/240V Power Compliance Matrix | By signing this form, the applicant declares that he/she has read and understands the provisions of Sections 620 and 996 of the FDOT Standard Specifications for Road and Bridge Construction and all implemented modifications. The requirements listed on this matrix are derived from Sections 620 and 996, and are the basis for determining a product’s compliance and its acceptability for use on Florida’s roads. |  |
| --- | --- | --- | --- |

| Date: | Click here to enter a date. | Applicant’s Name (print): |  |
| --- | --- | --- | --- |
| Manufacturer: |  |  |  |
| Item, Model No.: |  | Signature: |  |

|  |  | ** Greyed out rows in table below are for TERL use only ** |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ID No | Section | Requirement | Item Comply? (Yes/No/NA) | Comments (Applicant must provide information as indicated) | TERL Evaluation Method |
| 1 | 996-1.1 | SPD is permanently marked with manufacturer name or trademark, part number, and date of manufacture or serial number. |  | Applicant may provide comments in this field. | Physical Inspection |
|  |  | TERL Test Cases (Steps): SPD002 (Step 1) |  |  | Init.: |
| 2 | 996-4.2.2 | SPD includes L-N, L-G, and N-G protection. |  | Provide product literature, specifications, user manual, or similar information that shows the product meets this requirement. (Indicate specific configurations by model number or series). | Document Review |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (Step 1) |  |  | Init.: |
| 32 |  | SPD has a maximum surge current rating of 50kA per phase or greater. |  | Provide a first or third party test report that demonstrates compliance with this requirement. Also, provide a completed Testing Laboratory and Report Checklist. | Document Review |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (Step 2) |  |  | Init.: |
| 4 |  | SPD meets the requirements of UL 1449, Third Edition, and is listed by a Nationally Recognized Testing Laboratory (NRTL). |  | Provide a first or third party test report that demonstrates compliance with this requirement. Also, provide a completed Testing Laboratory and Report Checklist. Indicate listing (UL, ETL, etc.). | Document Review |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (Step 3) |  |  | Init.: |
| 5 |  | SPD has a visual indication system that monitors the weakest link in each mode and shows normal operation or failure status and also provides one set of normally open (NO)/normally closed (NC) Form C contacts for remote alarm monitoring. |  | Provide product literature, specifications, user manual, or similar information that shows the product meets this requirement. (Indicate specific configurations by model number or series). | Document Review and Physical Inspection |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (Step 4), SPD002 (Step 2) |  |  | Init.: |
| 6 |  | SPD enclosure has a NEMA 4 rating. |  | Applicant may provide comments in this field. | Compliance Matrix Review |
|  |  | TERL Test Cases (Steps): SPD001 (Step 5) |  |  | Init.: |
| 7 | 996-4.2.5 | All parts are made of corrosion-resistant materials, such as plastic, stainless steel, anodized aluminum, brass, or gold-plated metal. |  | Provide product literature, specifications, user manual, or similar information that shows the product meets this requirement. (Indicate specific configurations by model number or series). | Document Review and Physical Inspection |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (Step 6), SPD002 (Step 3) |  |  | Init.: |
| 8 | 996-4.2.6 | The SPD operates properly during and after being subjected to the environmental testing procedures described in NEMA TS 2, Sections 2.2.7, 2.2.8, and 2.2.9 |  | Provide a first or third party test report that demonstrates the device performs all required functions during and after being subjected to the environmental testing as described in NEMA TS2 section 2.2.7, 2.2.8, and 2.2.9. Also, provide a completed Testing Laboratory and Report Checklist and NEMA TS2 2.2.7-2.2.9 Checklist. | Document Review |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (Step 7) |  |  | Init.: |
| 9 | 620-2.7.1 | The SPD is intended for installation at the utility disconnect to the cabinet. |  | Provide product literature, specifications, user manual, or similar information that shows the product meets this requirement. (Indicate specific configurations by model number or series). | Document Review |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (Step 8) |  |  | Init.: |
| 10 | 620-2.7.4 | SPD has a manufacturer’s warranty covering defects for a minimum of 2 years from the date of final acceptance. |  | Provide product warranty documentation that shows the product meets this requirement. | Document Review |
|  |  |  |  | Indicate location of requested information in submittal. |  |
|  |  | TERL Test Cases (Steps): SPD001 (step 9) |  |  | Init.: |
| 11 |  | If the SPD, including any component of the unit, fails during the warranty period, the entire SPD is replaced by the manufacturer at no cost to the Department or maintaining agency. |  | Provide a statement of conformance in this field. | Compliance Matrix Review |
|  |  | TERL Test Cases (Steps): SPD001 (Step 10) |  |  | Init.: |

Document History for:

Surge Protective Device (SPD) for 120V or 120/240V Power Compliance Matrix

| Rev | Description | Authored and Checked | Reviewed | Approved | Approval Date | Rev More Stringent? |
| --- | --- | --- | --- | --- | --- | --- |
| 1.0 | New CM to correspond with specification content move from Section 785 to 620. This CM updates and replaces previous CM-785-2.2-01. Revised document approver title. | R. Meyer K. Moser | J. Morgan | J. Morgan | 10/27/2014 | No |
| 2.0 | Moved from Spec 620 to Spec 996-4.2. | W. Geitz | M. DeWitt J. Morgan | D. Vollmer | 01/30/2020 | No |
| 3.0 | Added warranty information. | W. Geitz | M. DeWitt C. Raimer | D. Vollmer | 12/29/2021 | No |
| 4.0 | Added test cases and steps, and updated to latest FA Date 10-24-22. | P. Blaiklock W. Geitz | P. Blaiklock W. Geitz | D. Vollmer | 02/23/2023 | No |
| 5.0 | Updated to latest FA dates of 9-13-23 and 12-1-23 for specs 620 and 996, respectively. | W. Geitz | L. Audisio | D. Vollmer | 01/08/2023 | No |
| 6.0 | Updated NEMA TS2 wording to match new spec language. Updated to latest FA date of 10-16-24 for 996. | W. Geitz | D. Bremer M. DeWitt | M. DeWitt | 03/06/2025 | No |